## CABLE DATA (OD)
TABEL DIAMETER LUAR KABEL (OUTER DIAMETER / OD)
Sel kuning = INPUT. Ganti angka OD di kolom C sesuai katalog pabrikan; seluruh workbook ikut ter-update otomatis.
Nilai di bawah adalah OD TIPIKAL pasaran Indonesia (Supreme/Kabelindo/Kabelmetal) - WAJIB DIVERIFIKASI ke katalog pabrikan sebelum konstruksi.
KODE TIPE | DESKRIPSI KABEL | OD (mm) | LUAS PENAMPANG (mm2) | KETERANGAN
3C-4 | 1x3C-4mm2 Cu/XLPE/PVC (N2XY) | 13.5 | 143.1388 | Tipikal N2XY 3x4mm2
5C-4 | 1x5C-4mm2 Cu/XLPE/PVC (N2XY) | 16 | 201.0619 | Tipikal N2XY 5x4mm2
4C-6 | 1x4C-6mm2 Cu/XLPE/PVC (N2XY) | 16 | 201.0619 | Incoming DB-UTILITY (DEG)
4C-25 | 1x4C-25mm2 Cu/XLPE/PVC (N2XY) | 27.5 | 593.9574 | Incoming DB-HVAC UTILITY / EMERGENCY
4C-70 | 1x4C-70mm2 Cu/XLPE/PVC (N2XY) | 34 | 907.9203 | Incoming DB-UTILITY
1C-6 | 1C-6mm2 Cu/PVC G/Y (NYA) | 5.5 | 23.7583 | Pembumian DB-UTILITY (DEG)
1C-16 | 1C-16mm2 Cu/PVC G/Y (NYA) | 8 | 50.2655 | Pembumian DB-HVAC UTILITY / EMERGENCY
1C-35 | 1C-35mm2 Cu/PVC G/Y (NYA) | 11 | 95.0332 | Pembumian DB-UTILITY
2C-2.5F | 1x2C-2.5mm2 Cu/MGT/XLPE/LSZH (FRC) | 11 | 95.0332 | Kabel fire alarm tahan api

## CABLE SCHEDULE
CABLE SCHEDULE - REKAP SELURUH KABEL DARI 3 GAMBAR PANEL SCHEDULE
Sumber: MEFLV6001 (DB-UTILITY & DB-UTILITY DEG), MEFLV6002 (DB-HVAC UTILITY), MEFLV6003 (DB-HVAC UTILITY EMERGENCY)
Kolom OD diambil otomatis dari sheet 'CABLE DATA (OD)' dengan INDEX/MATCH. Baris FUTURE/SPARE tidak diberi OD (jumlah run = 0).
NO | GAMBAR | PANEL | CIRCUIT No. | KATEGORI | SUPPLY FOR SYSTEM | DAYA (kW) | DESKRIPSI KABEL | KODE TIPE | JML RUN | OD (mm) | LEBAR TOTAL (mm) | LUAS TOTAL (mm2) | CATATAN
1 | MEFLV6001 | DB-UTILITY | FA-INTERLOCK | INCOMING | FIRE ALARM INTERLOCK | 0 | 1x2C-2.5mm2 Cu/MGT/XLPE/LSZH (FRC) | 2C-2.5F | 1 | 11 | 11 | 95.0332 | Interlock fire alarm - tray terpisah
2 | MEFLV6001 | DB-UTILITY | INCOMING | INCOMING | FEEDER PANEL | 0 | 1x4C-70mm2 Cu/XLPE/PVC | 4C-70 | 1 | 34 | 34 | 907.9203 | Feeder utama (Pact 65.52 kW), in cable tray/trunking. Daya diisi 0 agar total kW tidak dobel dgn outgoing.
3 | MEFLV6001 | DB-UTILITY | INCOMING-E | INCOMING | FEEDER PANEL | 0 | 1C-35mm2 Cu/PVC G/Y | 1C-35 | 1 | 11 | 11 | 95.0332 | Pembumian feeder utama
4 | MEFLV6001 | DB-UTILITY | DB-UTILTY-01 | OUTGOING | LIGHTING (F)/1 | 0.144 | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 3C-4 | 1 | 13.5 | 13.5 | 143.1388
5 | MEFLV6001 | DB-UTILITY | DB-UTILTY-02 | OUTGOING | LIGHTING (F)/2 | 2.7 | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 3C-4 | 1 | 13.5 | 13.5 | 143.1388
6 | MEFLV6001 | DB-UTILITY | DB-UTILTY-03 | OUTGOING | LIGHTING (F)/3 | 2.4 | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 3C-4 | 1 | 13.5 | 13.5 | 143.1388
7 | MEFLV6001 | DB-UTILITY | DB-UTILTY-04 | OUTGOING | LIGHTING (F)/4 | 1.35 | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 3C-4 | 1 | 13.5 | 13.5 | 143.1388
8 | MEFLV6001 | DB-UTILITY | DB-UTILTY-05 | OUTGOING | LIGHTING (F)/5 | 0.312 | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 3C-4 | 1 | 13.5 | 13.5 | 143.1388
9 | MEFLV6001 | DB-UTILITY | DB-UTILTY-06 | OUTGOING | LIGHTING (F)/6 | 0.8 | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 3C-4 | 1 | 13.5 | 13.5 | 143.1388
10 | MEFLV6001 | DB-UTILITY | DB-UTILTY-07 | OUTGOING | EXIT LIGHTING (F)/7 | 0.055 | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 3C-4 | 1 | 13.5 | 13.5 | 143.1388
11 | MEFLV6001 | DB-UTILITY | DB-UTILTY-08 | OUTGOING | EM. LIGHTING (F)/8 | 0.108 | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 3C-4 | 1 | 13.5 | 13.5 | 143.1388
12 | MEFLV6001 | DB-UTILITY | DB-UTILTY-09 | OUTGOING | RECEPTACLE (F)/9 | 0.6 | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 3C-4 | 1 | 13.5 | 13.5 | 143.1388
13 | MEFLV6001 | DB-UTILITY | DB-UTILTY-10 | OUTGOING | RECEPTACLE (F)/10 | 0.8 | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 3C-4 | 1 | 13.5 | 13.5 | 143.1388
14 | MEFLV6001 | DB-UTILITY | DB-UTILTY-11 | OUTGOING | FOR SHUTTER DOOR (F)/11 | 2.2 | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 3C-4 | 1 | 13.5 | 13.5 | 143.1388
15 | MEFLV6001 | DB-UTILITY | DB-UTILTY-12 | OUTGOING | RECEPTACLE (F)/12,13,14 | 9 | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 3C-4 | 1 | 13.5 | 13.5 | 143.1388
16 | MEFLV6001 | DB-UTILITY | DB-UTILTY-13 | OUTGOING | FOR SHUTTER DOOR (F)/15 | 2.2 | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 3C-4 | 1 | 13.5 | 13.5 | 143.1388
17 | MEFLV6001 | DB-UTILITY | DB-UTILTY-14 | OUTGOING | RECEPTACLE (F)/16,17,18 | 9 | 1x5C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 5C-4 | 1 | 16 | 16 | 201.0619
18 | MEFLV6001 | DB-UTILITY | DB-UTILTY-15 | OUTGOING | RECEPTACLE (F)/19 | 1 | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 3C-4 | 1 | 13.5 | 13.5 | 143.1388
19 | MEFLV6001 | DB-UTILITY | DB-UTILTY-16 | OUTGOING | RECEPTACLE (F)/20 | 1 | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 3C-4 | 1 | 13.5 | 13.5 | 143.1388
20 | MEFLV6001 | DB-UTILITY | DB-UTILTY-17 | OUTGOING | RECEPTACLE (F)/21 | 0.4 | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 3C-4 | 1 | 13.5 | 13.5 | 143.1388
21 | MEFLV6001 | DB-UTILITY | DB-UTILTY-18 | OUTGOING | RECEPTACLE (F)/22 | 0.8 | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 3C-4 | 1 | 13.5 | 13.5 | 143.1388
22 | MEFLV6001 | DB-UTILITY | DB-UTILTY-19 | OUTGOING | RECEPTACLE (F)/23,24,25 | 9 | 1x5C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 5C-4 | 1 | 16 | 16 | 201.0619
23 | MEFLV6001 | DB-UTILITY | DB-UTILTY-20 | OUTGOING | FOR SHUTTER DOOR (F)/26 | 2.2 | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 3C-4 | 1 | 13.5 | 13.5 | 143.1388
24 | MEFLV6001 | DB-UTILITY | DB-UTILTY-21 | OUTGOING | RECEPTACLE (F)/27,28,29 | 9 | 1x5C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 5C-4 | 1 | 16 | 16 | 201.0619
25 | MEFLV6001 | DB-UTILITY | DB-UTILTY-22 | OUTGOING | FOR SHUTTER DOOR (F)/30 | 2.2 | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 3C-4 | 1 | 13.5 | 13.5 | 143.1388
26 | MEFLV6001 | DB-UTILITY | DB-UTILTY-23 | OUTGOING | RECEPTACLE (F)/31 | 0.4 | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 3C-4 | 1 | 13.5 | 13.5 | 143.1388
27 | MEFLV6001 | DB-UTILITY | DB-UTILTY-24 | OUTGOING | RECEPTACLE (F)/32 | 0.4 | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 3C-4 | 1 | 13.5 | 13.5 | 143.1388
28 | MEFLV6001 | DB-UTILITY | DB-UTILTY-25 | OUTGOING | RECEPTACLE (F)/33 | 0.4 | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 3C-4 | 1 | 13.5 | 13.5 | 143.1388
29 | MEFLV6001 | DB-UTILITY | DB-UTILTY-26 | OUTGOING | FOR SHUTTER DOOR (F)/34 | 2.2 | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 3C-4 | 1 | 13.5 | 13.5 | 143.1388
30 | MEFLV6001 | DB-UTILITY | DB-UTILTY-27 | OUTGOING | SPARE / FUTURE | 0 | FUTURE |  | 0 | 0 | 0 | 0 | Circuit FUTURE/SPARE - belum ada kabel
31 | MEFLV6001 | DB-UTILITY | DB-UTILTY-28 | OUTGOING | SPARE / FUTURE | 0 | FUTURE |  | 0 | 0 | 0 | 0 | Circuit FUTURE/SPARE - belum ada kabel
32 | MEFLV6001 | DB-UTILITY | DB-UTILTY-29 | OUTGOING | SPARE / FUTURE | 0 | FUTURE |  | 0 | 0 | 0 | 0 | Circuit FUTURE/SPARE - belum ada kabel
33 | MEFLV6001 | DB-UTILITY (DEG) | INCOMING | INCOMING | FEEDER PANEL | 0 | 1x4C-6mm2 Cu/XLPE/PVC | 4C-6 | 1 | 16 | 16 | 201.0619 | Feeder dari DEG (Pact 7.99 kW). Daya diisi 0 agar total kW tidak dobel.
34 | MEFLV6001 | DB-UTILITY (DEG) | INCOMING-E | INCOMING | FEEDER PANEL | 0 | 1C-6mm2 Cu/PVC G/Y | 1C-6 | 1 | 5.5 | 5.5 | 23.7583 | Pembumian feeder DEG
35 | MEFLV6001 | DB-UTILITY (DEG) | DB-UTILTY-30 | OUTGOING | RECEPTACLE (F)/35 | 0.8 | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 3C-4 | 1 | 13.5 | 13.5 | 143.1388
36 | MEFLV6001 | DB-UTILITY (DEG) | DB-UTILTY-31 | OUTGOING | RECEPTACLE (F)/36 | 0.4 | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 3C-4 | 1 | 13.5 | 13.5 | 143.1388
37 | MEFLV6001 | DB-UTILITY (DEG) | DB-UTILTY-32 | OUTGOING | RECEPTACLE (F)/37 FIRE ALARM | 2 | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 3C-4 | 1 | 13.5 | 13.5 | 143.1388
38 | MEFLV6001 | DB-UTILITY (DEG) | DB-UTILTY-33 | OUTGOING | RECEPTACLE (F)/38 PUBLIC ADDRESS | 2 | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 3C-4 | 1 | 13.5 | 13.5 | 143.1388
39 | MEFLV6001 | DB-UTILITY (DEG) | DB-UTILTY-34 | OUTGOING | RECEPTACLE (F)/39 CCTV | 2 | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 3C-4 | 1 | 13.5 | 13.5 | 143.1388
40 | MEFLV6001 | DB-UTILITY (DEG) | DB-UTILTY-35 | OUTGOING | RECEPTACLE (F)/40 | 0.2 | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 3C-4 | 1 | 13.5 | 13.5 | 143.1388
41 | MEFLV6001 | DB-UTILITY (DEG) | DB-UTILTY-36 | OUTGOING | SPARE / FUTURE | 0 | FUTURE |  | 0 | 0 | 0 | 0 | Circuit FUTURE/SPARE - belum ada kabel
42 | MEFLV6001 | DB-UTILITY (DEG) | DB-UTILTY-37 | OUTGOING | SPARE / FUTURE | 0 | FUTURE |  | 0 | 0 | 0 | 0 | Circuit FUTURE/SPARE - belum ada kabel
43 | MEFLV6001 | DB-UTILITY (DEG) | DB-UTILTY-38 | OUTGOING | SPARE / FUTURE | 0 | FUTURE |  | 0 | 0 | 0 | 0 | Circuit FUTURE/SPARE - belum ada kabel
44 | MEFLV6002 | DB-HVAC UTILITY | INCOMING | INCOMING | FEEDER PANEL | 0 | 1x4C-25mm2 Cu/XLPE/PVC | 4C-25 | 1 | 27.5 | 27.5 | 593.9574 | Feeder utama (Pact 36.24 kW), in cable tray/trunking. Daya diisi 0 agar total kW tidak dobel.
45 | MEFLV6002 | DB-HVAC UTILITY | INCOMING-E | INCOMING | FEEDER PANEL | 0 | 1C-16mm2 Cu/PVC G/Y | 1C-16 | 1 | 8 | 8 | 50.2655 | Pembumian feeder
46 | MEFLV6002 | DB-HVAC UTILITY | DB-HVAC-01 | OUTGOING | IU F-001 WORKSHOP (F-005) | 0.1 | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 3C-4 | 1 | 13.5 | 13.5 | 143.1388
47 | MEFLV6002 | DB-HVAC UTILITY | DB-HVAC-02 | OUTGOING | IU F-101 OFFICE (F-101) | 0.2 | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 3C-4 | 1 | 13.5 | 13.5 | 143.1388
48 | MEFLV6002 | DB-HVAC UTILITY | DB-HVAC-03 | OUTGOING | IU F-102 SUPERVISOR RM (F-102) | 0.016 | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 3C-4 | 1 | 13.5 | 13.5 | 143.1388
49 | MEFLV6002 | DB-HVAC UTILITY | DB-HVAC-04 | OUTGOING | IU F-103 MANAGER RM (F-103) | 0.016 | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 3C-4 | 1 | 13.5 | 13.5 | 143.1388
50 | MEFLV6002 | DB-HVAC UTILITY | DB-HVAC-05 | OUTGOING | OU F-001 MMY-MUP1201T8(J)P | 7.61 | 1x5C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 5C-4 | 1 | 16 | 16 | 201.0619
51 | MEFLV6002 | DB-HVAC UTILITY | DB-HVAC-06 | OUTGOING | EF F 001.01 NH3 PLANT (F-004) | 9.52 | 1x5C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 5C-4 | 1 | 16 | 16 | 201.0619
52 | MEFLV6002 | DB-HVAC UTILITY | DB-HVAC-07 | OUTGOING | EF F 002 STEAM PLANT (F-005) | 7.5 | 1x5C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 5C-4 | 1 | 16 | 16 | 201.0619
53 | MEFLV6002 | DB-HVAC UTILITY | DB-HVAC-08 | OUTGOING | EF F 003 WATER TREAT. (F-006) | 7.5 | 1x5C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 5C-4 | 1 | 16 | 16 | 201.0619
54 | MEFLV6002 | DB-HVAC UTILITY | DB-HVAC-09 | OUTGOING | EF F 005 CHEMICAL ROOM (F-007) | 0.55 | 1x5C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 5C-4 | 1 | 16 | 16 | 201.0619
55 | MEFLV6002 | DB-HVAC UTILITY | DB-HVAC-10 | OUTGOING | EF F 006 Archetype Cambodia Ltd. JANITOR & TOILETS (F-006,7, | 0.55 | 1x5C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 5C-4 | 1 | 16 | 16 | 201.0619
56 | MEFLV6002 | DB-HVAC UTILITY | DB-HVAC-11 | OUTGOING | SPARE / FUTURE | 0 | FUTURE |  | 0 | 0 | 0 | 0 | Circuit FUTURE/SPARE - belum ada kabel
57 | MEFLV6002 | DB-HVAC UTILITY | DB-HVAC-12 | OUTGOING | SPARE / FUTURE | 0 | FUTURE |  | 0 | 0 | 0 | 0 | Circuit FUTURE/SPARE - belum ada kabel
58 | MEFLV6002 | DB-HVAC UTILITY | DB-HVAC-13 | OUTGOING | SPARE / FUTURE | 0 | FUTURE |  | 0 | 0 | 0 | 0 | Circuit FUTURE/SPARE - belum ada kabel
59 | MEFLV6003 | DB-HVAC UTILITY EMERGENCY | FA-INTERLOCK | INCOMING | FIRE ALARM INTERLOCK | 0 | 1x2C-2.5mm2 Cu/MGT/XLPE/LSZH (FRC) | 2C-2.5F | 1 | 11 | 11 | 95.0332 | Interlock fire alarm - tray terpisah
60 | MEFLV6003 | DB-HVAC UTILITY EMERGENCY | INCOMING | INCOMING | FEEDER PANEL | 0 | 1x4C-25mm2 Cu/XLPE/PVC | 4C-25 | 1 | 27.5 | 27.5 | 593.9574 | Feeder utama (Pact 28.66 kW), in cable tray/trunking. Daya diisi 0 agar total kW tidak dobel.
61 | MEFLV6003 | DB-HVAC UTILITY EMERGENCY | INCOMING-E | INCOMING | FEEDER PANEL | 0 | 1C-16mm2 Cu/PVC G/Y | 1C-16 | 1 | 8 | 8 | 50.2655 | Pembumian feeder
62 | MEFLV6003 | DB-HVAC UTILITY EMERGENCY | DB-HVAC-EMG-1 | OUTGOING | EF F 001.02 NH3 PLANT (F-004) | 9.52 | 1x5C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 5C-4 | 1 | 16 | 16 | 201.0619
63 | MEFLV6003 | DB-HVAC UTILITY EMERGENCY | DB-HVAC-EMG-2 | OUTGOING | EF F 001.03 NH3 PLANT (F-004) | 9.52 | 1x5C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 5C-4 | 1 | 16 | 16 | 201.0619
64 | MEFLV6003 | DB-HVAC UTILITY EMERGENCY | DB-HVAC-EMG-3 | OUTGOING | EF F 004.02 CO2+COMPR. AIR (F-002) | 7.5 | 1x5C-4mm2 Cu/XLPE/PVC INCLUDING (E) | 5C-4 | 1 | 16 | 16 | 201.0619
65 | MEFLV6003 | DB-HVAC UTILITY EMERGENCY | DB-HVAC-EMG-4 | OUTGOING | SPARE / FUTURE | 0 | FUTURE |  | 0 | 0 | 0 | 0 | Circuit FUTURE/SPARE - belum ada kabel
66 | MEFLV6003 | DB-HVAC UTILITY EMERGENCY | DB-HVAC-EMG-5 | OUTGOING | SPARE / FUTURE | 0 | FUTURE |  | 0 | 0 | 0 | 0 | Circuit FUTURE/SPARE - belum ada kabel
67 | MEFLV6003 | DB-HVAC UTILITY EMERGENCY | DB-HVAC-EMG-6 | OUTGOING | SPARE / FUTURE | 0 | FUTURE |  | 0 | 0 | 0 | 0 | Circuit FUTURE/SPARE - belum ada kabel
TOTAL | [5 empty] | 128.171 |  |  | 55 |  | 797 | 9842.6098

## SUMMARY BY TYPE
REKAPITULASI KABEL
A. REKAP PER TIPE KABEL
KODE TIPE | DESKRIPSI KABEL | OD (mm) | JML RUN | LEBAR TOTAL (mm) | LUAS TOTAL (mm2) | % THD LEBAR
3C-4 | 1x3C-4mm2 Cu/XLPE/PVC (N2XY) | 13.5 | 33 | 445.5 | 4723.5809 | 55.9%
5C-4 | 1x5C-4mm2 Cu/XLPE/PVC (N2XY) | 16 | 12 | 192 | 2412.7432 | 24.09%
4C-6 | 1x4C-6mm2 Cu/XLPE/PVC (N2XY) | 16 | 1 | 16 | 201.0619 | 2.008%
4C-25 | 1x4C-25mm2 Cu/XLPE/PVC (N2XY) | 27.5 | 2 | 55 | 1187.9147 | 6.901%
4C-70 | 1x4C-70mm2 Cu/XLPE/PVC (N2XY) | 34 | 1 | 34 | 907.9203 | 4.266%
1C-6 | 1C-6mm2 Cu/PVC G/Y (NYA) | 5.5 | 1 | 5.5 | 23.7583 | 0.6901%
1C-16 | 1C-16mm2 Cu/PVC G/Y (NYA) | 8 | 2 | 16 | 100.531 | 2.008%
1C-35 | 1C-35mm2 Cu/PVC G/Y (NYA) | 11 | 1 | 11 | 95.0332 | 1.38%
2C-2.5F | 1x2C-2.5mm2 Cu/MGT/XLPE/LSZH (FRC) | 11 | 2 | 22 | 190.0664 | 2.76%
TOTAL |  |  | 55 | 797 | 9842.6098 | 100%
B. REKAP PER PANEL
PANEL | GAMBAR | JML CIRCUIT | JML RUN | TOTAL DAYA (kW) | LEBAR TOTAL (mm) | LUAS TOTAL (mm2)
DB-UTILITY | MEFLV6001 | 32 | 29 | 60.669 | 414.5 | 4993.3652
DB-UTILITY (DEG) | MEFLV6001 | 11 | 8 | 7.4 | 102.5 | 1083.6531
DB-HVAC UTILITY | MEFLV6002 | 15 | 12 | 33.562 | 185.5 | 2423.1497
DB-HVAC UTILITY EMERGENCY | MEFLV6003 | 9 | 6 | 26.54 | 94.5 | 1342.4418
TOTAL |  | 67 | 55 | 128.171 | 797 | 9842.6098

## TRAY CALCULATION
PERHITUNGAN UKURAN & JUMLAH JALUR CABLE TRAY
Proyek: Panel Schedule DB-UTILITY / DB-HVAC UTILITY / DB-HVAC UTILITY EMERGENCY ¦ Sel KUNING = input yang boleh diubah
A. PARAMETER PERHITUNGAN (INPUT - SEL KUNING)
A1 | Faktor spare / cadangan pengembangan | 30% | - | Praktik umum 20-30%. Menyediakan ruang untuk penambahan kabel di kemudian hari.
A2 | Faktor jarak antar kabel | 1.1 | - | 1.00 = kabel bersentuhan rapat. 1.10 = ada jarak 10% untuk pendinginan & kerapian.
A3 | Tinggi / kedalaman tray | 100 | mm | Standar pasaran: 50 / 100 / 150 mm.
A4 | Maksimum fill ratio (rasio pengisian) | 40% | - | Batas umum 40% luas penampang tray (NEC 392 / praktik industri).
A5 | Jumlah layer / susunan kabel | 1 | layer | 1 layer = single layer (disarankan). >1 layer WAJIB koreksi KHA (derating).
A6 | Lebar tray standar yang dipilih | 600 | mm | Lebar tray yang akan dipakai di lapangan. Lihat tabel alternatif di blok F.
B. REKAP DATA KABEL (otomatis dari sheet CABLE SCHEDULE)
B1 | Jumlah baris circuit / feeder terdata | 67 | baris | Termasuk incoming, pembumian, FRC, dan circuit FUTURE.
B2 | Jumlah RUN kabel aktif (Σ jumlah run) | 55 | run | Circuit FUTURE/SPARE = 0 run (belum ada kabel).
B3 | Total lebar kabel Σ OD | 797 | mm | Σ (OD x jumlah run) seluruh kabel.
B4 | Total luas penampang kabel Σ A | 9842.6098 | mm2 | Σ (π/4 x OD² x jumlah run) seluruh kabel.
B5 | Total daya terpasang | 128.171 | kW | Jumlah daya seluruh panel (referensi, tidak dipakai dalam sizing tray).
C. METODE 1 - PENJUMLAHAN DIAMETER (Σ OD)
Rumus: W1 = Σ OD x faktor jarak x (1 + faktor spare) / jumlah layer
C1 | Σ OD seluruh kabel | 797 | mm | Dari B3.
C2 | Setelah faktor jarak antar kabel | 876.7 | mm | C1 x A2.
C3 | Setelah faktor spare | 1139.71 | mm | C2 x (1 + A1).
C4 | LEBAR TRAY DIBUTUHKAN - METODE 1 | 1139.71 | mm | C3 dibagi jumlah layer (A5).
D. METODE 2 - FILL RATIO / LUAS PENAMPANG
Rumus: W2 = Σ A x (1 + faktor spare) / fill ratio / tinggi tray / jumlah layer
D1 | Σ A (luas penampang seluruh kabel) | 9842.6098 | mm2 | Dari B4.
D2 | Setelah faktor spare | 12795.3927 | mm2 | D1 x (1 + A1).
D3 | Luas tray minimum (setelah fill ratio) | 31988.4818 | mm2 | D2 dibagi fill ratio maksimum (A4).
D4 | LEBAR TRAY DIBUTUHKAN - METODE 2 | 319.8848 | mm | D3 dibagi tinggi tray (A3) dan jumlah layer (A5).
E. HASIL AKHIR & PENGECEKAN
E1 | LEBAR TRAY DIBUTUHKAN (menentukan) | 1139.71 | mm | Diambil nilai TERBESAR antara Metode 1 (C4) dan Metode 2 (D4).
E2 | Metode yang menentukan | METODE 1 - Σ OD | - | Untuk susunan 1 layer, Metode 1 hampir selalu menentukan.
E3 | Lebar tray standar dipilih | 600 | mm | Dari A6.
E4 | JUMLAH JALUR TRAY DIBUTUHKAN | 2 | jalur | Lebar dibutuhkan (E1) dibagi lebar tray dipilih (A6), dibulatkan ke atas.
E5 | Total lebar tray terpasang | 1200 | mm | Jumlah jalur (E4) x lebar tray (A6).
E6 | Luas tray tersedia | 120000 | mm2 | Jumlah jalur x lebar x tinggi x jumlah layer.
E7 | FILL RATIO AKTUAL | 8.202% | - | Σ A kabel (B4) dibagi luas tray tersedia (E6).
E8 | CEK TERHADAP BATAS FILL RATIO | OK | - | Fill aktual harus <= fill ratio maksimum (A4).
E9 | Okupansi lebar aktual (Σ OD / lebar terpasang) | 66.42% | - | Berapa persen lebar tray benar-benar tertutup kabel (belum termasuk spare).
F. TABEL ALTERNATIF LEBAR TRAY STANDAR x JUMLAH LAYER
Jumlah jalur = ROUNDUP( lebar dibutuhkan / lebar tray / layer , 0 ). Lebar dibutuhkan mengikuti parameter blok A kecuali jumlah layer.
| LEBAR TRAY (mm) | LEBAR DIBUTUHKAN (mm) | JALUR - 1 LAYER | JALUR - 2 LAYER | JALUR - 3 LAYER | FILL AKTUAL 1 LAYER | CEK 1 LAYER
| 100 | 1139.71 | 12 | 6 | 4 | 8.202% | OK
| 150 | 1139.71 | 8 | 4 | 3 | 8.202% | OK
| 200 | 1139.71 | 6 | 3 | 2 | 8.202% | OK
| 300 | 1139.71 | 4 | 2 | 2 | 8.202% | OK
| 400 | 1139.71 | 3 | 2 | 1 | 8.202% | OK
| 500 | 1139.71 | 3 | 2 | 1 | 6.562% | OK
| 600 | 1139.71 | 2 | 1 | 1 | 8.202% | OK
| 750 | 1139.71 | 2 | 1 | 1 | 6.562% | OK
| 800 | 1139.71 | 2 | 1 | 1 | 6.152% | OK
| 900 | 1139.71 | 2 | 1 | 1 | 5.468% | OK
| 1000 | 1139.71 | 2 | 1 | 1 | 4.921% | OK
G. PERHITUNGAN PER PANEL (bila rute tray dipisah per panel)
Dipakai jika kabel tiap panel TIDAK digabung dalam satu rute tray. Parameter mengikuti blok A.
| PANEL | Σ OD (mm) | Σ A (mm2) | LEBAR DIBUTUHKAN (mm) | JALUR (lebar A6) | FILL AKTUAL | CEK
| DB-UTILITY | 414.5 | 4993.3652 | 592.735 | 1 | 8.322% | OK
| DB-UTILITY (DEG) | 102.5 | 1083.6531 | 146.575 | 1 | 1.806% | OK
| DB-HVAC UTILITY | 185.5 | 2423.1497 | 265.265 | 1 | 4.039% | OK
| DB-HVAC UTILITY EMERGENCY | 94.5 | 1342.4418 | 135.135 | 1 | 2.237% | OK
| TOTAL (rute digabung) | 797 | 9842.6098 | 1139.71 | 2 | 8.202% | 4 | <- kolom H = total jalur bila rute DIPISAH per panel
H. CATATAN & ASUMSI (WAJIB DIBACA)
| Sumber gambar | MEFLV6001 - PANEL SCHEDULE DB-UTILITY (berisi 2 panel: DB-UTILITY dan DB-UTILITY FROM DEG); MEFLV6002 - PANEL SCHEDULE DB-HVAC UTILITY; MEFLV6003 - PANEL SCHEDULE DB-HVAC UTILITY EMERGENCY.
| Jumlah circuit | Total 57 circuit outgoing terekstrak (DB-UTILTY-01 s/d -29 = DB-UTILITY; DB-UTILTY-30 s/d -38 = DB-UTILITY DEG; DB-HVAC-01 s/d -13; DB-HVAC-EMG-1 s/d -6), ditambah 10 baris incoming/pembumian/FRC = 67 baris.
| Circuit FUTURE / SPARE | 12 circuit berstatus FUTURE/SPARE (DB-UTILTY-27,28,29,36,37,38; DB-HVAC-11,12,13; DB-HVAC-EMG-4,5,6) belum memiliki kabel sehingga jumlah run = 0. Kebutuhan ruangnya ditutup oleh faktor spare 30% pada blok A1.
| Verifikasi ekstraksi | Total daya hasil ekstraksi per panel dicocokkan dengan nilai Pt pada gambar: DB-UTILITY 60.67 vs Pt 60.66 kW; DB-UTILITY (DEG) 7.40 vs Pt 7.40 kW; DB-HVAC UTILITY 33.56 vs Pt 33.56 kW; DB-HVAC UTILITY EMERGENCY 26.54 vs Pt 26.50 kW. Selisih < 0.05 kW = pembulatan pada gambar.
| Daya incoming | Baris INCOMING diisi daya 0 kW agar total tidak dobel dengan outgoing. Pact tiap panel: DB-UTILITY 65.52 kW; DEG 7.99 kW; DB-HVAC UTILITY 36.24 kW; DB-HVAC UTILITY EMERGENCY 28.66 kW (setelah Ku 0.9 + spare 20%).
| Nilai OD | OD pada sheet CABLE DATA (OD) masih NILAI TIPIKAL pasaran Indonesia. WAJIB DIVERIFIKASI ke katalog pabrikan (Supreme / Kabelindo / Kabelmetal) sebelum dipakai untuk konstruksi. Ganti angka di sel kuning, seluruh perhitungan ikut ter-update.
| Panjang rute TIDAK dihitung | Perhitungan ini menghasilkan LEBAR dan JUMLAH JALUR tray, BUKAN volume/panjang material tray. Untuk BQ material (panjang tray, elbow, tee, support, hanger) diperlukan gambar denah / layout rute tray.
| Asumsi rute gabungan | Blok C, D, dan E mengasumsikan SELURUH kabel dari 3 gambar melewati SATU rute tray (kondisi paling berat). Bila rute dipisah per panel, gunakan blok G.
| Kabel FRC fire alarm | Kabel 1x2C-2.5mm2 Cu/MGT/XLPE/LSZH (FRC) untuk interlock fire alarm HARUS dipisahkan tray-nya atau diberi sekat (barrier) dari kabel daya, sesuai persyaratan sistem proteksi kebakaran.
| Susunan lebih dari 1 layer | Bila jumlah layer > 1, WAJIB diterapkan faktor koreksi grouping sesuai PUIL 2011 / IEC 60364-5-52 terhadap KHA kabel. Perhitungan ini hanya menghitung ruang fisik, bukan derating arus.
| Fill ratio rendah pada 1 layer | Untuk susunan 1 layer, Metode 1 (Σ OD) hampir selalu menentukan dan fill ratio aktual keluar rendah (sekitar 10%). Ini BENAR, bukan kesalahan hitung - tray 1 layer memang tidak diisi sampai 40% luas.
| Kabel pembumian | Kabel pembumian G/Y (1C-35mm2, 1C-16mm2, 1C-6mm2) dihitung sebagai run terpisah karena diletakkan berdampingan dengan kabel feeder di dalam tray.
| Daya | Kolom daya (kW) hanya sebagai referensi identifikasi beban; tidak dipakai dalam perhitungan ukuran tray.