## DB-RMW-L0-LP
HANUMAN BREWERY EXPANSION PHASE 3 RAW MATERIAL_REV3
DB-RMW-L0-LP
BOX PANEL - LOCATION raw material 1
220/380V, 3PH, 4W, 50Hz - cos phi 0.8
cos phi |  | 0.8
V (L-L) |  | 380
V (L-N) |  | 220
NO. | FUNCTION | BREAKER | TYPE | FIXTURE | [29 empty] | DEMAND LOAD (WATT) |  |  | REMARKS | AMPERE | BREAKER SELECTION | OD (mm)
|  |  |  | ACT_E_DOWNLIGHT 12W DOWNLIGHT 12WATT NORMAL | ACT_E_DOWNLIGHT 12W DOWNLIGHT 12WATT EMERGENCY | ACT_E_DOWNLIGHT 24WATT DOWNLIGHT 24 WATT | ACT_E_DOWNLIGHT 24WATT DOWNLIGHT 24 WATT W/ BATTERY | ACT_E_DOWNLIGHT SURFACE 12W DOWNLIGHT 12 C/W BATTERY | ACT_E_DOWNLIGHT SURFACE 12W DOWNLIGHT SURFACE 12W | ACT_E_EXIT LIGHTING ARROW EXIT LIGHTING ARROW 5WATT | ACT_E_EXIT LIGHTING DOUBLE SIGN ARROW EXIT LIGHTING DOUBLE LEFT RIGHT ARROW 5WATT | ACT_E_EXIT LIGHTING EXIT LIGHTING 5WATT | ACT_E_HIGHBAY_150 WATT HIGHBAY 150W NRML | ACT_E_EMERGENCY LAMP 6WATT EMERGENCY LIGHT 2X6 WATT | ACT_E_LED TUBE_SURFACE 18WATT_ SURFACE 18WATT | ACT_E_LED TUBE_SURFACE 18WATT_ SURFACE 18WATT W/BATTERY | ACT_E_LED TUBE_SURFACE 2_18WATT SURFACE 40WATT | ACT_E_LED TUBE_SURFACE 2_18WATT SURFACE 40WATT W/BATTERY | ACT_E_LIGHTING RECESSED RECESSED 40WATT NORMAL | ACT_E_LIGHTING RECESSED RECESSED 40WATT EMERGENCY | ACT_INSECT KILLER_ ACT_E_INSECT KILLER LAMP | ACT_E_ISOLATOR SWICTH 1PH ISOLATOR SWITCH 1PH | ACT_E_ISOLATOR SWICTH 3PH ISOLATOR SWITCH 3PH | ACT_E_ISOLATOR SWICTH 3PH ISOLATOR SWITCH 3PH FOR CHARGING STATION | ACT_E_POP UP FOR TABLE 1 SOCKET POP UP FLOOR 1 SOCKET | ACT_E_POP UP FOR TABLE 1 SOCKET POP UP FLOOR 1 SOCKET FOR EMERGENCY | ACT_E_POWER OUTLET FLUSH NORMAL | ACT_E_POWER OUTLET FLUSH EMERGENCY | ACT_E_POWER OUTLET FLUSH FOR VESDA VESDA | ACT_E_POWER OUTLET FLUSH HAND DRYER | ACT_E_RECEPTACLE GENERAL COVER IP56 1PH ACT_E_RECEPTACLE GENERAL COVER IP56 1PH | ACT_E_RECEPTACLE INDUSTRIAL 1PH | ACT_E_RECEPTACLE INDUSTRIAL 3PH | R (WATT) | S (WATT) | T (WATT)
WATT / UNIT |  |  |  | 12 | 12 | 24 | 24 | 14 | 14 | 5 | 5 | 5 | 150 | 6 | 18 | 18 | 40 | 40 | 40 | 40 | 30 | 2200 | 3000 | 22000 | 200 | 200 | 200 | 200 | 200 | 1000 | 200 | 200 | 9000
1 | LIGHTING (E)/1 | MCB 1P 10A | NYY 3C x 2.5mm2 | [9 empty] | 9 | [20 empty] | 1350 |  |  |  | 6.14 | 10A | 14
2 | LIGHTING (E)/2 | MCB 1P 10A | NYY 3C x 2.5mm2 | [9 empty] | 10 | [21 empty] | 1500 |  |  | 6.82 | 10A | 14
3 | LIGHTING (E)/3 | MCB 1P 10A | NYY 3C x 2.5mm2 | [9 empty] | 8 | [22 empty] | 1200 |  | 5.45 | 10A | 14
4 | LIGHTING (E)/4 | MCB 1P 10A | NYY 3C x 2.5mm2 | [9 empty] | 10 | [20 empty] | 1500 |  |  |  | 6.82 | 10A | 14
5 | LIGHTING (E)/5 | MCB 1P 10A | NYY 3C x 2.5mm2 | [9 empty] | 8 | [21 empty] | 1200 |  |  | 5.45 | 10A | 14
6 | LIGHTING (E)/6 | MCB 1P 10A | NYY 3C x 2.5mm2 | [9 empty] | 9 | [22 empty] | 1350 |  | 6.14 | 10A | 14
7 | LIGHTING (E)/7 | MCB 1P 10A | NYY 3C x 2.5mm2 | [9 empty] | 8 | [20 empty] | 1200 |  |  |  | 5.45 | 10A | 14
8 | LIGHTING (E)/8 | MCB 1P 10A | NYY 3C x 2.5mm2 | [9 empty] | 8 | [21 empty] | 1200 |  |  | 5.45 | 10A | 14
9 | LIGHTING (E)/9 | MCB 1P 10A | NYY 3C x 2.5mm2 | [9 empty] | 8 | [22 empty] | 1200 |  | 5.45 | 10A | 14
10 | LIGHTING (E)/10 | MCB 1P 10A | NYY 3C x 2.5mm2 | [9 empty] | 8 | [20 empty] | 1200 |  |  |  | 5.45 | 10A | 14
11 | LIGHTING (E)/11 | MCB 1P 10A | NYY 3C x 2.5mm2 | [9 empty] | 7 | [21 empty] | 1050 |  |  | 4.77 | 10A | 14
12 | LIGHTING (E)/12 | MCB 1P 10A | NYY 3C x 2.5mm2 | [9 empty] | 8 | [22 empty] | 1200 |  | 5.45 | 10A | 14
13 | LIGHTING (E)/13 | MCB 1P 10A | NYY 3C x 2.5mm2 | [9 empty] | 8 | [20 empty] | 1200 |  |  |  | 5.45 | 10A | 14
14 | LIGHTING (E)/14 | MCB 1P 10A | NYY 3C x 2.5mm2 | [9 empty] | 8 | [21 empty] | 1200 |  |  | 5.45 | 10A | 14
15 | LIGHTING (E)/15 | MCB 1P 10A | NYY 3C x 2.5mm2 | [9 empty] | 8 | [22 empty] | 1200 |  | 5.45 | 10A | 14
16 | LIGHTING (E)/16 | MCB 1P 10A | NYY 3C x 2.5mm2 | [9 empty] | 10 | [20 empty] | 1500 |  |  |  | 6.82 | 10A | 14
17 | LIGHTING (E)/17 | MCB 1P 10A | NYY 3C x 2.5mm2 | [9 empty] | 5 |  |  |  | 1 | 1 | [16 empty] | 830 |  |  | 3.77 | 10A | 14
18 | LIGHTING (E)/18 | MCB 1P 10A | NYY 3C x 2.5mm2 | [9 empty] | 6 | [22 empty] | 900 |  | 4.09 | 10A | 14
19 | LIGHTING (E)/19 | MCB 1P 10A | NYY 3C x 2.5mm2 | [9 empty] | 6 | [20 empty] | 900 |  |  |  | 4.09 | 10A | 14
20 | LIGHTING (E)/20 | MCB 1P 10A | NYY 3C x 2.5mm2 | [9 empty] | 2 | [21 empty] | 300 |  |  | 1.36 | 10A | 14
21 | LIGHTING (E)/21 | MCB 1P 10A | NYY 3C x 2.5mm2 | 3 | 2 | 7 | 2 | [28 empty] | 276 |  | 1.25 | 10A | 14
22 | LIGHTING (E)/22 | MCB 1P 10A | NYY 3C x 2.5mm2 | 7 | 2 | 2 | 1 | 1 | 2 | [24 empty] | 216 |  |  |  | 0.98 | 10A | 14
23 | LIGHTING (E)/23 | MCB 1P 10A | NYY 3C x 2.5mm2 | [11 empty] | 4 | 2 |  |  | 7 | 3 | [14 empty] | 508 |  |  | 2.31 | 10A | 14
24 | LIGHTING (E)/24 | MCB 1P 10A | NYY 3C x 2.5mm2 |  |  | 2 | 1 | [11 empty] | 6 | 2 | [15 empty] | 392 |  | 1.78 | 10A | 14
25 | LIGHTING (E)/25 | MCB 1P 10A | NYY 3C x 2.5mm2 | [15 empty] | 12 | 4 | [13 empty] | 640 |  |  |  | 2.91 | 10A | 14
26 | LIGHTING (E)/26 | MCB 1P 10A | NYY 3C x 2.5mm2 | 4 | 2 | [13 empty] | 4 | 2 | [14 empty] | 312 |  |  | 1.42 | 10A | 14
27 | LIGHTING (E)/27 | MCB 1P 10A | NYY 3C x 2.5mm2 | [9 empty] | 9 | [22 empty] | 1350 |  | 6.14 | 10A | 14
28 | LIGHTING (E)/28 | MCB 1P 10A | NYY 3C x 2.5mm2 | [10 empty] | 22 | [19 empty] | 132 |  |  |  | 0.6 | 10A | 14
29 | LIGHTING (E)/29 | MCB 1P 10A | NYY 3C x 2.5mm2 | [10 empty] | 12 | [20 empty] | 72 |  |  | 0.33 | 10A | 14
30 | LIGHTING (E)/30 | MCB 1P 10A | NYY 3C x 2.5mm2 | [10 empty] | 13 | [21 empty] | 78 |  | 0.35 | 10A | 14
31 | LIGHTING (E)/31 | MCB 1P 10A | NYY 3C x 2.5mm2 | [6 empty] | 9 |  | 3 | [21 empty] | 60 |  |  |  | 0.27 | 10A | 14
32 | LIGHTING (E)/32 | MCB 1P 10A | NYY 3C x 2.5mm2 | [6 empty] | 1 | 1 | 9 | [22 empty] | 55 |  |  | 0.25 | 10A | 14
33 | LIGHTING (E)/33 | MCB 1P 10A | NYY 3C x 2.5mm2 | [17 empty] | 13 | [14 empty] | 390 |  | 1.77 | 10A | 14
34 | RECEPTACLE (E)/34 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [28 empty] | 5 |  | 1000 |  |  |  | 4.55 | 10A | 16.1
35 | RECEPTACLE (E)/35 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [28 empty] | 3 |  |  | 600 |  |  | 2.73 | 10A | 16.1
36 | RECEPTACLE (E)/36 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [18 empty] | 1 | [13 empty] | 2200 |  | 10 | 10A | 16.1
37 | RECEPTACLE (E)/37 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [18 empty] | 1 | [11 empty] | 2200 |  |  |  | 10 | 10A | 16.1
38 | RECEPTACLE (E)/38 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [28 empty] | 2 |  |  | 400 |  |  | 1.82 | 10A | 16.1
39 | RECEPTACLE (E)/39 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [18 empty] | 1 | [13 empty] | 2200 |  | 10 | 10A | 16.1
40 | RECEPTACLE (E)/40 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [18 empty] | 1 | [11 empty] | 2200 |  |  |  | 10 | 10A | 16.1
41 | RECEPTACLE (E)/41 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [18 empty] | 1 | [12 empty] | 2200 |  |  | 10 | 10A | 16.1
42 | RECEPTACLE (E)/42 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [18 empty] | 1 | [13 empty] | 2200 |  | 10 | 10A | 16.1
43 | RECEPTACLE (E)/43 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [18 empty] | 1 | [11 empty] | 2200 |  |  |  | 10 | 10A | 16.1
44 | RECEPTACLE (E)/44 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [18 empty] | 1 | [12 empty] | 2200 |  |  | 10 | 10A | 16.1
45 | RECEPTACLE (E)/45 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [18 empty] | 1 | [13 empty] | 2200 |  | 10 | 10A | 16.1
46 | RECEPTACLE (E)/46 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [18 empty] | 1 | [11 empty] | 2200 |  |  |  | 10 | 10A | 16.1
47 | RECEPTACLE (E)/47,48,49 | RCCB 4P 20A 30mA | NYY 5C x 4mm2 | [29 empty] | 1 | 3000 | 3000 | 3000 |  | 17.09 | 20A | 18.7
48 | RECEPTACLE (E)/50,51,52 | RCCB 4P 16A 30mA | NYY 5C x 4mm2 | [19 empty] | 1 | [10 empty] | 1000 | 1000 | 1000 |  | 5.7 | 10A | 18.7
49 | RECEPTACLE (E)/53,54,55 | RCCB 4P 16A 30mA | NYY 5C x 4mm2 | [19 empty] | 1 | [10 empty] | 1000 | 1000 | 1000 |  | 5.7 | 10A | 18.7
50 | RECEPTACLE (E)/56,57,58 | RCCB 4P 16A 30mA | NYY 5C x 4mm2 | [19 empty] | 1 | [10 empty] | 1000 | 1000 | 1000 |  | 5.7 | 10A | 18.7
51 | RECEPTACLE (E)/59,60,61 | RCCB 4P 16A 30mA | NYY 5C x 4mm2 | [19 empty] | 1 | [10 empty] | 1000 | 1000 | 1000 |  | 5.7 | 10A | 18.7
52 | RECEPTACLE (E)/62,63,64 | RCCB 4P 16A 30mA | NYY 5C x 4mm2 | [19 empty] | 1 | [10 empty] | 1000 | 1000 | 1000 |  | 5.7 | 10A | 18.7
53 | RECEPTACLE (E)/65,66,67 | RCCB 4P 16A 30mA | NYY 5C x 4mm2 | [19 empty] | 1 | [10 empty] | 1000 | 1000 | 1000 |  | 5.7 | 10A | 18.7
54 | RECEPTACLE (E)/68,69,70 | RCCB 4P 16A 30mA | NYY 5C x 4mm2 | [19 empty] | 1 | [10 empty] | 1000 | 1000 | 1000 |  | 5.7 | 10A | 18.7
55 | RECEPTACLE (E)/71,72,73 | RCCB 4P 16A 30mA | NYY 5C x 4mm2 | [19 empty] | 1 | [10 empty] | 1000 | 1000 | 1000 |  | 5.7 | 10A | 18.7
56 | RECEPTACLE (E)/74,75,76 | RCCB 4P 50A 30mA | NYY 5C x 6mm2 | [20 empty] | 1 | [9 empty] | 7333.3 | 7333.3 | 7333.3 |  | 41.78 | 50A | 20.5
57 | RECEPTACLE (E)/77,78,79 | RCCB 4P 50A 30mA | NYY 5C x 6mm2 | [20 empty] | 1 | [9 empty] | 7333.3 | 7333.3 | 7333.3 |  | 41.78 | 50A | 20.5
58 | RECEPTACLE (E)/80 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [18 empty] | 1 | [12 empty] | 2200 |  |  | 10 | 10A | 16.1
59 | RECEPTACLE (E)/81 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [26 empty] | 1 | [5 empty] | 1000 |  | 4.55 | 10A | 16.1
60 | RECEPTACLE (E)/82 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [21 empty] | 4 | [8 empty] | 800 |  |  |  | 3.64 | 10A | 16.1
61 | RECEPTACLE (E)/83 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [23 empty] | 2 | [7 empty] | 400 |  |  | 1.82 | 10A | 16.1
62 | RECEPTACLE (E)/84 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [26 empty] | 1 | [5 empty] | 1000 |  | 4.55 | 10A | 16.1
63 | RECEPTACLE (E)/85 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [26 empty] | 1 |  |  |  | 1000 |  |  |  | 4.55 | 10A | 16.1
64 | RECEPTACLE (E)/86 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [21 empty] | 4 | [9 empty] | 800 |  |  | 3.64 | 10A | 16.1
65 | RECEPTACLE (E)/87 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [21 empty] | 3 |  | 1 | [8 empty] | 800 |  | 3.64 | 10A | 16.1
66 | RECEPTACLE (E)/88 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [21 empty] | 2 | [8 empty] | 400 |  |  |  | 1.82 | 10A | 16.1
67 | RECEPTACLE (E)/89 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [27 empty] | 2 |  |  |  | 400 |  |  | 1.82 | 10A | 16.1
68 | RECEPTACLE (E)/90 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [21 empty] | 1 |  | 2 | [8 empty] | 600 |  | 2.73 | 10A | 16.1
69 | RECEPTACLE (E)/91 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [21 empty] | 6 | [8 empty] | 1200 |  |  |  | 5.45 | 10A | 16.1
70 | RECEPTACLE (E)/92 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [23 empty] | 1 | [7 empty] | 200 |  |  | 0.91 | 10A | 16.1
71 | RECEPTACLE (E)/93 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [23 empty] | 1 | [8 empty] | 200 |  | 0.91 | 10A | 16.1
72 | RECEPTACLE (E)/94 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [23 empty] | 1 | [6 empty] | 200 |  |  |  | 0.91 | 10A | 16.1
73 | RECEPTACLE (E)/95 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [22 empty] | 4 | [8 empty] | 800 |  |  | 3.64 | 10A | 16.1
74 | RECEPTACLE (E)/96 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [22 empty] | 4 |  | 1 | [7 empty] | 1000 |  | 4.55 | 10A | 16.1
75 | RECEPTACLE (E)/97 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [22 empty] | 3 | [7 empty] | 600 |  |  |  | 2.73 | 10A | 16.1
76 | RECEPTACLE (E)/98 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [22 empty] | 6 | [8 empty] | 1200 |  |  | 5.45 | 10A | 16.1
77 | RECEPTACLE (E)/99 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [22 empty] | 3 | [9 empty] | 600 |  | 2.73 | 10A | 16.1
78 | RECEPTACLE (E)/100 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [23 empty] | 1 | [6 empty] | 200 |  |  |  | 0.91 | 10A | 16.1
79 | RECEPTACLE (E)/101 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [25 empty] | 1 | [5 empty] | 200 |  |  | 0.91 | 10A | 16.1
80 | RECEPTACLE (E)/102 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [25 empty] | 1 | [6 empty] | 200 |  | 0.91 | 10A | 16.1
81 | RECEPTACLE (E)/103 | RCBO 2P 16A 30mA | NYY 3C x 4mm2 | [25 empty] | 1 |  |  |  |  | 200 |  |  |  | 0.91 | 10A | 16.1
TOTAL |  |  |  | 14 | 6 | 11 | 4 | 1 | 2 | 10 | 1 | 12 | 163 | 47 | 4 | 2 | 1 | 1 | 29 | 11 | 13 | 11 | 8 | 2 | 20 | 20 | 9 | 1 | 3 | 3 | 2 | 10 | 1
SUB TOTAL | [33 empty] | 49964.6 | 45493.6 | 49402.6
TOTAL WATT | [33 empty] | 144860.8
TOTAL VA | [33 empty] | 181076
CONNECTED AMPERE | [33 empty] | 275.1
Rumus perhitungan (angka di kolom DEMAND LOAD & baris ringkasan adalah formula Excel, ikut berubah kalau data diedit):
DEMAND LOAD R/S/T per circuit = SUMPRODUCT(qty kolom FIXTURE x baris WATT / UNIT di baris 11), dibagi rata ke fase yang berbeban (mis. /3 untuk circuit 3 fase seimbang)
Semua kolom FIXTURE sudah punya angka WATT / UNIT.
1 circuit tetap memakai angka demand load dari Revit (angka mati, bukan formula) karena bebannya tidak berasal dari fixture di tabel ini — mis. beban langsung dari equipment — jadi qty x watt/unit tidak akan pernah sama dengan nilai Revit.
SUB TOTAL R/S/T (AI94..AK94) = SUM per kolom fase, baris 12-92
TOTAL WATT (AI95) = SUB TOTAL R + S + T
TOTAL VA (AI96) = TOTAL WATT / cos phi (sel C5)
CONNECTED AMPERE (AI97) = TOTAL VA / (SQRT(3) x V L-L) (sel C6)
AMPERE per circuit = SUM(R,S,T) / V(L-N) sel C7 untuk circuit 1 fase, dan / (cos phi x SQRT(3) x V L-L) untuk circuit 3 fase
BREAKER SELECTION = rating standar terdekat yang masih di ATAS AMPERE circuit (10, 16, 20, 25, 35, 40, 50, 63, 80, 100, 125, 160, 200 A) — ikut berubah kalau ampere-nya berubah. Ini usulan ukuran breaker, tetap perlu dicek terhadap KHA kabel & jenis bebannya.
BREAKER = jenis breaker menurut jenis bebannya + rating dari BREAKER SELECTION: LIGHTING MCB 1P minimum 10A; RECEPTACLE 1 fase RCBO 2P 30mA minimum 16A; RECEPTACLE 3 fase RCCB 4P 30mA minimum 16A. Ditulis sebagai formula, jadi ikut berubah kalau ampere-nya berubah.
TYPE & OD = kabel NYY katalog PT KMI Wire and Cable (IEC 60502-1, 0,6/1 kV) — ukuran terkecil yang KHA-nya di udara (30 °C) masih di atas rating breaker, minimum LIGHTING NYY 3C x 2.5mm2, RECEPTACLE 1 fase NYY 3C x 4mm2, RECEPTACLE 3 fase NYY 5C x 4mm2. OD = overall diameter kabel itu (mm) dari katalog yang sama.
Sel berwarna kuning (cos phi C5, tegangan C6 & C7, baris WATT / UNIT 11) boleh diisi/diubah — angka di bawahnya ikut menyesuaikan.